## Sheet1
1 | TECHNICAL DATA SHEET – DISTRIBUTION CLASS (LIGHT DUTY– 5kA Porcelain)
ARRESTER MODEL REFERENCE
| PARTICULARS | 3DVNE | 6DVNE | 9DVNE | 12DVNE | 15DVNE | 18DVNE | 21DVNE | 24DVNE | 27DVNE | 30DVNE | 33DVNE | 36DVNE
| System Voltage (kVrms) | 3.3 | 6.6 | 11 | 11 | 22 | 22 | 22 | 24 | 33 | 33 | 33 | 33
| Rating (kVrms) | 3 | 6 | 9 | 12 | 15 | 18 | 21 | 24 | 27 | 30 | 33 | 36
| MCOV (kVrms) | 2.55 | 5.1 | 7.65 | 10.2 | 12.75 | 15.3 | 17.85 | 20.4 | 22.95 | 25.5 | 28.05 | 30.6
| Nominal Discharge Current (kAp) | 3: 5
| Line Discharge Class | 3: DISTRIBUTION
| Rated Frequency (Hz) | 3: 50
Insulation withstand level
| Lightning Impulse withstand (kVp) | 60 | 60 | 75 | 75 | 125 | 125 | 125 | 125 | 170 | 170 | 170 | 170
| Power Frequency withstand | 20 | 20 | 28 | 28 | 50 | 50 | 50 | 50 | 70 | 70 | 70 | 70
(Dry/Wet) (kVrms)
| Reference Voltage (kVrms) | >3.0 | >6.0 | >9.0 | >12.0 | >15.0 | >18.0 | >21.0 | >24.0 | >27.0 | >30.0 | >33.0 | >36.0
Reference Current (mAp) | bar: 3
Maximum Lightning Impulse
Residual Voltage (8/20μs ) at NDC
(kVp)
| At 2.5kAp | 7.4 | 14.8 | 28 | 37.3 | 46.7 | 56 | 65.3 | 74.7 | 84 | 93.3 | 102.7 | 112
| At 5.0kAp | 8 | 16 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 | 110 | 120
| At 10.0kAp | 9.1 | 18.2 | 32 | 42.7 | 53.3 | 64 | 74.7 | 85.3 | 96 | 106.7 | 117.3 | 128
| Max. Steep current impulse residual | 8.2 | 16.4 | 24.6 | 32.8 | 41.1 | 49.3 | 57.5 | 65.7 | 73.9 | 82.1 | 90.3 | 98.5
voltage (1/20μs) at NDC (kVp)
Temporary Over Voltage Capability
(kVrms) at
| 1.0 sec | 3.6 | 7.2 | 10.6 | 14.13 | 17.67 | 21.6 | 24.73 | 28.27 | 31.8 | 35.33 | 38.87 | 42.4
| 10.0 sec | 3.45 | 6.9 | 10.1 | 13.46 | 16.83 | 20.7 | 23.57 | 26.93 | 30.3 | 33.67 | 37.03 | 40.4
| 100.0 sec | 3.3 | 6.6 | 9.7 | 12.93 | 16.17 | 19.8 | 22.63 | 25.87 | 29.1 | 32.33 | 35.57 | 38.8
| High Current Impulse Withstand(kA) | 8.2: 65
| Long Duration Current Withstand(A) | 8.2: 150
| Partial Discharge (pC) | 8.2: <10.0
| Minimum Creepage Distance (mm) | 250 | 250 | 300 | 300 | 600 | 600 | 600 | 600 | 900 | 900 | 900 | 900
Leakage Current at MCOV
| Resistive Current (μA) | 8.2: <300
| Capacitive Current (μA) | 8.2: ~1000
| Cantilever Strength (Kg.m) | 8.2: 200
| Pressure Relief Class | 8.2: N.A (Disconnector Type)
| Diameter of the Arrester (mm) | 8.2: 110 +/- 5
| Height of the Arrester (mm) | 105 | 105 | 350 | 350 | 505 | 505 | 505 | 505 | 650 | 650 | 650 | 650
| Weight of the Arrester (Kgs) | 0.65 | 0.8 | 2.5 | 3 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9
2 | TECHNICAL DATA SHEET – STATION CLASS 1 (10kA - Porcelain)
ARRESTER MODEL REFERENCE
| PARTICULARS | 3SX1NE | 6SX1NE | 9SX1NE | 12SX1NE | 15SX1NE | 18SX1NE | 21SX1NE | 24SX1NE | 27SX1NE | 30SX1NE | 33SX1NE | 36SX1NE
| System Voltage (kVrms) | 3.3 | 6.6 | 11 | 11 | 22 | 22 | 22 | 24 | 33 | 33 | 33 | 33
| Rating (kVrms) | 3 | 6 | 9 | 12 | 15 | 18 | 21 | 24 | 27 | 30 | 33 | 36
| MCOV (kVrms) | 2.55 | 5.1 | 7.65 | 10.2 | 12.75 | 15.3 | 17.85 | 20.4 | 22.95 | 25.5 | 28.05 | 30.6
| Nominal Discharge Current (kAp) | 3: 10
| Line Discharge Class | 3: STATION CLASS 1
| Rated Frequency (Hz) | 3: 50
Insulation withstand level
| Lightning Impulse withstand (kVp) | 60 | 60 | 75 | 75 | 125 | 125 | 125 | 125 | 170 | 170 | 170 | 170
| Power Frequency withstand | 20 | 20 | 28 | 28 | 50 | 50 | 50 | 50 | 70 | 70 | 70 | 70
(Dry/Wet) (kVrms)
| Reference Voltage (kVrms) | >3.0 | >6.0 | >9.0 | >12.0 | >15.0 | >18.0 | >21.0 | >24.0 | >27.0 | >30.0 | >33.0 | >36.0
Reference Current (mAp) | bar: 3
Maximum Lightning Impulse
Residual Voltage (8/20μs ) at NDC
(kVp)
| At 2.5kAp | 7.4 | 14.8 | 28 | 36.3 | 46.9 | 56 | 65.5 | 74.5 | 84.3 | 93.1 | 102.4 | 112.1
| At 5.0kAp | 8.1 | 16.2 | 30.1 | 39 | 50 | 60 | 70.1 | 80 | 90 | 100 | 110 | 120
| At 10.0kAp | 9 | 18.1 | 32.1 | 42.2 | 53.1 | 64 | 74.4 | 85.5 | 96 | 106.5 | 117.4 | 128
| Max. Steep current impulse residual | 10.2 | 20.3 | 35.1 | 42.2 | 58.2 | 70.1 | 81.5 | 93.2 | 105.1 | 116.5 | 128.2 | 140
voltage (1/20μs) at NDC (kVp)
Temporary Over Voltage Capability
(kVrms) at
| 1.0 sec | 3.7 | 6.72 | 10.2 | 13.5 | 16.4 | 20.2 | 23.6 | 26.9 | 30.5 | 33.7 | 37 | 40.45
| 10.0 sec | 3.4 | 6.3 | 9.4 | 12.5 | 15.2 | 18.8 | 21.9 | 25.1 | 28.3 | 31.3 | 34.6 | 37.5
| 100.0 sec | 3.4 | 5.5 | 8.6 | 11.5 | 14.1 | 17.2 | 20.1 | 22.9 | 25.8 | 28.7 | 31.4 | 34.5
| High Current Impulse Withstand(kA) | 3: 100
| Long Duration Current Withstand(A) | 3: 250
| Partial Discharge (pC) | 3: <10.0
| Minimum Creepage Distance (mm) | 250 | 250 | 300 | 300 | 600 | 600 | 600 | 600 | 900 | 900 | 900 | 900
Leakage Current at MCOV
| Resistive Current (μA) | 3: <400
| Capacitive Current (μA) | 3: ~1200
| Cantilever Strength (Kg.m) | 3: 200
| Pressure Relief Class | 3: CLASS A
| Pressure Relief Currrent (kArms) | 3: 40
| Diameter of the Arrester (mm) | 3: 150 +/- 5.0
| Height of the Arrester (mm) | 150 | 150 | 390 | 390 | 500 | 500 | 500 | 500 | 570 | 570 | 570 | 570
| Weight of the Arrester (Kgs) | 4 | 5.5 | 6.7 | 7.5 | 10 | 10.9 | 11.5 | 12.3 | 13 | 13.5 | 14.1 | 14.5
3 | TECHNICAL DATA SHEET – STATION CLASS 2 (10kA - Porcelain)
ARRESTER MODEL REFERENCE
| PARTICULARS | 3SX2NE | 6SX2NE | 9SX2NE | 12SX2NE | 15SX2NE | 18SX2NE | 21SX2NE | 24SX2NE | 27SX2NE | 30SX2NE | 33SX2NE | 36SX2NE
| System Voltage (kVrms) | 3.3 | 6.6 | 11 | 11 | 22 | 22 | 22 | 24 | 33 | 33 | 33 | 33
| Rating (kVrms) | 3 | 6 | 9 | 12 | 15 | 18 | 21 | 24 | 27 | 30 | 33 | 36
| MCOV (kVrms) | 2.55 | 5.1 | 7.65 | 10.2 | 12.75 | 15.3 | 17.85 | 20.4 | 22.95 | 25.5 | 28.05 | 30.6
| Nominal Discharge Current (kAp) | 3: 10
| Line Discharge Class | 3: STATION CLASS 2
| Rated Frequency (Hz) | 3: 50
Insulation withstand level
| Lightning Impulse withstand (kVp) | 60 | 60 | 75 | 75 | 125 | 125 | 125 | 125 | 170 | 170 | 170 | 170
| Power Frequency withstand | 20 | 20 | 28 | 28 | 50 | 50 | 50 | 50 | 70 | 70 | 70 | 70
(Dry/Wet) (kVrms)
| Reference Voltage (kVrms) | >3.0 | >6.0 | >9.0 | >12.0 | >15.0 | >18.0 | >21.0 | >24.0 | >27.0 | >30.0 | >33.0 | >36.0
| Reference Current (mAp) | 3: 2
Maximum Lightning Impulse
Residual Voltage (8/20μs ) at NDC
(kVp)
| At 5.0kAp | 7.4 | 14.8 | 24.1 | 32 | 40.7 | 48 | 56.3 | 65.1 | 73 | 81 | 89 | 97.5
| At 10.0kAp | 8.1 | 16.2 | 26.3 | 35.2 | 44.3 | 53 | 62.2 | 71 | 80 | 89 | 97.9 | 107
| At 20.0kAp | 9 | 17.9 | 29 | 39.1 | 49.2 | 59 | 68.9 | 78.3 | 88.2 | 102.2 | 108.2 | 118.2
| Max. Steep current impulse residual | 10.2 | 20.3 | 30.1 | 42.2 | 51.2 | 61.1 | 72 | 82.2 | 92.5 | 102.8 | 113.1 | 123.4
voltage (1/20μs) at NDC (kVp)
| Max Switching Impulse Residual | 6.7 | 13.4 | 20.2 | 27.1 | 33.8 | 40.5 | 47.3 | 54.1 | 62.5 | 67.5 | 74.3 | 81.2
voltage (30/60μs impulse) at 500 A
Temporary Over Voltage Capability
(kVrms) at
| 1.0 sec | 3.6 | 6.6 | 10.3 | 13.5 | 16.4 | 20.3 | 23.7 | 27 | 30.5 | 33.5 | 37.2 | 40.6
| 10.0 sec | 3.4 | 6.3 | 9.4 | 12.6 | 15.4 | 18.7 | 21.6 | 25.6 | 28.4 | 31.7 | 34.9 | 37.2
| 100.0 sec | 3.3 | 5.7 | 8.6 | 11.8 | 14.3 | 17.3 | 20.5 | 23.5 | 25.9 | 28.6 | 31.8 | 34.7
| High Current Impulse Withstand(kA) | 3: 100
| Long Duration Current Withstand(A) | 3: 250
| Partial Discharge (pC) | 3: <10.0
| Minimum Creepage Distance (mm) | 250 | 250 | 300 | 300 | 600 | 600 | 600 | 600 | 900 | 900 | 900 | 900
Leakage Current at MCOV
| Resistive Current (μA) | 3: <400
| Capacitive Current (μA) | 3: ~1200
| Cantilever Strength (Kg.m) | 3: 325
| Pressure Relief Class | 3: CLASS A
| Pressure Relief Currrent (kArms) | 3: 40
| Diameter of the Arrester (mm) | 3: 150 +/- 5.0
| Height of the Arrester (mm) | 150 | 150 | 390 | 390 | 500 | 500 | 500 | 500 | 570 | 570 | 570 | 570
| Weight of the Arrester (Kgs) | 4.2 | 5.7 | 6.7 | 7.7 | 10.2 | 10.8 | 11.2 | 11.9 | 12.8 | 13.1 | 13.9 | 14.2
4 | TECHNICAL DATA SHEET – DISTRIBUTION & STATION CLASS (Indoor Polymer - 5kA & 10kA)
ARRESTER MODEL REFERENCE
| PARTICULARS - DIST CLASS - 5 kA | 3DVNE | 6DVNE | 9DVNE | 12DVNE | 15DVNE | 18DVNE | 21DVNE | 24DVNE | 27DVNE | 30DVNE | 33DVNE | 36DVNE
| PARTICULARS -STN CLASS-10kA | 3SXNE | 6SXNE | 9SXNE | 12SXNE | 15SXNE | 18SXNE | 21SXNE | 24SXNE | 27SXNE | 30SXNE | 33SXNE | 36SXNE
| System Voltage (kVrms) | 3.3 | 6.6 | 11 | 11 | 22 | 22 | 22 | 24 | 33 | 33 | 33 | 33
| Rating (kVrms) | 3 | 6 | 9 | 12 | 15 | 18 | 21 | 24 | 27 | 30 | 33 | 36
| MCOV (kVrms) | 2.55 | 5.1 | 7.65 | 10.2 | 12.75 | 15.3 | 17.85 | 20.4 | 22.95 | 25.5 | 28.05 | 30.6
| Nominal Discharge Current (kAp) | 3: 5 & 10
| Line Discharge Class | 3: DISTRIBUTION & STATION CLASS
| Rated Frequency (Hz) | 3: 50
Insulation withstand level
| Lightning Impulse withstand (kVp) | 60 | 60 | 75 | 75 | 125 | 125 | 125 | 125 | 170 | 170 | 170 | 170
| Power Frequency withstand | 20 | 20 | 28 | 28 | 50 | 50 | 50 | 50 | 70 | 70 | 70 | 70
(Dry/Wet) (kVrms)
| Reference Voltage (kVrms) | >3.0 | >6.0 | >9.0 | >12.0 | >15.0 | >18.0 | >21.0 | >24.0 | >27.0 | >30.0 | >33.0 | >36.0
Reference Current (mAp) | bar: 3
Maximum Lightning Impulse
Residual Voltage (8/20μs ) at NDC
(kVp)
| At 2.5kAp | 7.4 | 14.8 | 28 | 37.3 | 46.7 | 56 | 65.3 | 74.7 | 84 | 93.3 | 102.7 | 112
| At 5.0kAp | 8 | 16 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 | 110 | 120
| At 10.0kAp | 9.1 | 18.2 | 32 | 42.7 | 53.3 | 64 | 74.7 | 85.3 | 96 | 106.7 | 117.3 | 128
| Max. Steep current impulse residual | 8.2 | 16.4 | 24.6 | 32.8 | 41.1 | 49.3 | 57.5 | 65.7 | 73.9 | 82.1 | 90.3 | 98.5
voltage (1/20μs) at NDC (kVp)
Temporary Over Voltage Capability
(kVrms) at
| 1.0 sec | 3.6 | 7.2 | 10.6 | 14.13 | 17.67 | 21.6 | 24.73 | 28.27 | 31.8 | 35.33 | 38.87 | 42.4
| 10.0 sec | 3.45 | 6.9 | 10.1 | 13.46 | 16.83 | 20.7 | 23.57 | 26.93 | 30.3 | 33.67 | 37.03 | 40.4
| 100.0 sec | 3.3 | 6.6 | 9.7 | 12.93 | 16.17 | 19.8 | 22.63 | 25.87 | 29.1 | 32.33 | 35.57 | 38.8
| High Current Impulse Withstand(kA) | 8.2: 65
| Long Duration Current Withstand(A) | 8.2: 150
| Partial Discharge (pC) | 8.2: <10.0
Leakage Current at MCOV
| Resistive Current (μA) | 8.2: <300
| Capacitive Current (μA) | 8.2: ~1000
| Cantilever Strength (Kg.m) | 8.2: 200
| Diameter of the Arrester (mm) | 8.2: 52 +/- 2
| Height of the Arrester (mm) | 100 | 150 | 180 | 210 | 260 | 305 | 350 | 400 | 420 | 495 | 535 | 580
| Weight of the Arrester (Kgs) | 1 | 1.2 | 2.5 | 3 | 4.7 | 5.3 | 6.2 | 6.8 | 7 | 7.3 | 7.5 | 8.4
5 | TECHNICAL DATA SHEET – DISTRIBUTION & STATION CLASS (Outdoor Polymer 5kA & 10kA)
ARRESTER MODEL REFERENCE
| PARTICULARS - DIST CLASS - 5 kA | 8.2: 6DVNE; 16.4: 9DVNE; 24.6: 12DVNE; 32.8: 27DVNE; 41.1: 30DVNE; 49.3: 33DVNE
| PARTICULARS -STN CLASS-10kA | 8.2: 6SXNE; 16.4: 9SXNE; 24.6: 12SXNE; 32.8: 27SXNE; 41.1: 30SXNE; 49.3: 33SXNE
| System Voltage (kVrms) | 8.2: 6.6; 16.4: 11; 24.6: 11; 32.8: 33; 41.1: 33; 49.3: 33
| Rating (kVrms) | 6 | 9 | 12 | 27 | 30 | 33
| MCOV (kVrms) | 5.1 | 7.65 | 10.2 | 22.95 | 25.5 | 28.05
| Nominal Discharge Current (kAp) | 6: 5 & 10
| Line Discharge Class | 6: DISTRIBUTION & STATION CLASS
| Rated Frequency (Hz) | 6: 50
Insulation withstand level
| Lightning Impulse withstand (kVp) | 60 | 75 | 75 | 170 | 170 | 170
| Power Frequency withstand | 20 | 28 | 28 | 70 | 70 | 70
(Dry/Wet) (kVrms)
| Reference Voltage (kVrms) | >6.0 | >9.0 | >12.0 | >27.0 | >30.0 | >33.0
Reference Current (mAp) | bar: 6
Maximum Lightning Impulse
Residual Voltage (8/20μs ) at NDC
(kVp)
| At 2.5kAp | 14.8 | 28 | 37.3 | 84 | 93.3 | 102.7
| At 5.0kAp | 16 | 30 | 40 | 90 | 100 | 110
| At 10.0kAp | 18.2 | 32 | 42.7 | 96 | 106.7 | 117.3
| Max. Steep current impulse residual | 16.4 | 24.6 | 32.8 | 73.9 | 82.1 | 90.3
voltage (1/20μs) at NDC (kVp)
Temporary Over Voltage Capability
(kVrms) at
| 1.0 sec | 7.2 | 10.6 | 14.13 | 31.8 | 35.33 | 38.87
| 10.0 sec | 6.9 | 10.1 | 13.46 | 30.3 | 33.67 | 37.03
| 100.0 sec | 6.6 | 9.7 | 12.93 | 29.1 | 32.33 | 35.57
| High Current Impulse Withstand(kA) | 6: 65
| Long Duration Current Withstand(A) | 6: 150
| Partial Discharge (pC) | 6: <10.0
| Resistive Current (μA) | 6: <300
| Capacitive Current (μA) | 6: ~1000
| Cantilever Strength (Kg.m) | 6: 200
| Diameter of the Arrester (mm) | 6: 90 & 115